# TempCtl v2.0.1 - Controller Requirements (for markup)

Status: describes the controller as shipped in TempCtl v2.0.1 (2026-09-12), the version behind the current TempSim.exe. Every statement below is implemented and covered by the unit tests; the normative source is src/tempctl.h. Numbered items are there so a markup can say "change R3.4" or "add R6.5". Words in code are the names used in the header and the simulator.

## 1. Scope and interface

- R1.1 The controller is pure signals in, signals out. It owns no hardware and no CAN. One call per control tick: TcStep(zone, action, nowMs, in[17], out[27]).

- R1.2 zone selects one of 16 independent controllers (0..15). Zones share nothing.

- R1.3 action is Init (0), Step (1) or Reset (2). See section 9.

- R1.4 nowMs is a free-running millisecond tick (LabVIEW Tick Count (ms)). The controller differences successive values; wrap-around at 2^32 is handled. The absolute value has no meaning.

- R1.5 in and out are SGL arrays. in needs at least 17 elements, out at least 27. They may be the same array.

- R1.6 Configuration is live: every input is read on every call, a change takes effect on the next Step, no re-Init.

- R1.7 The DLL (x64, x86) and the .so (x86_64 cRIO, aarch64 and armhf Pi) are built from the same source with a plain C interface (cdecl), no dependencies beyond libc.

- R1.8 TcVersion() returns 2.0.1 as (major<<16)|(minor<<8)|patch; TcInputCount() = 17 and TcSignalCount() = 27 let the caller size arrays.

## 2. Inputs (in[0..16])

| # | Name | Unit | Meaning |
| --- | --- | --- | --- |
| 0 | Setpoint | deg | Target. Heating runs until ControlTemp >= Setpoint, cooling until <= Setpoint. |
| 1 | DeadbandHi | deg, >= 0 | HiBand = Setpoint + DeadbandHi. |
| 2 | DeadbandLo | deg, >= 0 | LoBand = Setpoint - DeadbandLo. |
| 3 | HiLimit | deg | A sensor above this for ErrorTimeout has failed high. |
| 4 | LoLimit | deg | A sensor below this for ErrorTimeout has failed low. |
| 5 | ErrorTimeout | ms, >= 0 | Countdown length for every fault condition (limits, bad reading, disagreement, relay feedback). |
| 6 | DeadbandTimeout | ms, >= 0 | Time ControlTemp must sit outside the band before a relay engages. |
| 7 | FilterPoints | 1..64 | Moving-average length per sensor. 0 means 4. |
| 8 | Temp2Enable | 0/1 | Second sensor present: rationality check, disagreement check and failover. |
| 9 | Temp2Tolerance | deg, >= 0 | Allowed difference between the two filtered sensors. |
| 10 | FeedbackEnable | 0/1 | Compare the relay feedback inputs with the commands. |
| 11 | Temp1 | deg | Sensor 1, the primary. NaN/Inf = bad reading (open thermocouple). |
| 12 | Temp2 | deg | Sensor 2. Ignored unless Temp2Enable. |
| 13 | HeaterFeedback | 0/1 | Measured heater relay state. Ignored unless FeedbackEnable. |
| 14 | CoolerFeedback | 0/1 | Measured cooler relay state. |
| 15 | HeatingCmd | 0/1 | Read on Init only: relay state the controller starts from. |
| 16 | CoolingCmd | 0/1 | Read on Init only. If both are 1, heating wins. |

Boolean inputs are true when > 0.5.

## 3. Outputs (out[0..26])

- R3.1 out[0..14] echo the inputs unchanged, so the whole array can go to CAN (the 27-signal layout is the TempCtl DBC message, PGN 65280).

- R3.2 out[15] HeatingCmd and out[16] CoolingCmd are the relay commands for this tick, never both 1.

| # | Name | Meaning |
| --- | --- | --- |
| 17 | ErrorStatus | Bit mask, section 8. |
| 18 | TempStatus | State code 0..8, section 7. |
| 19 | ControlTemp | Filtered value of the active sensor; the value control acts on. |
| 20 | Temp1Filtered | Moving average of sensor 1. NaN until the first valid sample. |
| 21 | Temp2Filtered | Moving average of sensor 2. NaN when Temp2Enable = 0 or no valid sample yet. |
| 22 | HiBand | Setpoint + DeadbandHi. |
| 23 | LoBand | Setpoint - DeadbandLo. |
| 24 | ErrorRemainMs | Smallest error countdown still running; 0 when none (or stopped). |
| 25 | DbRemainMs | Remaining deadband countdown; 0 when idle in band or while a relay is on. |
| 26 | ActiveSensor | 1 or 2: the sensor whose filtered value is ControlTemp. |

## 4. Filtering and warm-up

- R4.1 Each sensor has its own moving average of FilterPoints samples. Only valid samples (not NaN, not Inf) enter it; a bad sample is skipped, it does not corrupt the average.

- R4.2 The filtered value is NaN until the first valid sample, then the average of the samples present (fewer than FilterPoints during warm-up).

- R4.3 TempStatus reports WARMUP (8) while the active sensor's filter holds fewer than FilterPoints samples. Control still runs on the partial average during warm-up.

- R4.4 Filters are also fed on Init and Reset (the sample passed with that call counts). Init clears the filter history; Reset keeps it.

- R4.5 Changing FilterPoints at run time takes effect immediately on the next average (the 64-sample history is always kept).

## 5. Sensor limits, bad readings, failover

- R5.1 Sensor 1 is always checked. Sensor 2 is checked only when Temp2Enable = 1. A sensor that has already failed is not re-checked.

- R5.2 Per sensor and per tick one condition is derived, first match wins: bad (raw NaN/Inf, or no filtered value yet), else high (filtered > HiLimit), else low (filtered < LoLimit), else none.

- R5.3 A condition starts a countdown of ErrorTimeout ms at the first Step that observes it. If the condition changes (for example high -> none, or high -> bad) the countdown restarts from full or clears. When the countdown reaches 0 the sensor has failed and the matching bit latches (T1_HI, T1_LO, T1_BAD, T2_HI, T2_LO, T2_BAD).

- R5.4 ErrorTimeout = 0 latches on the first observation.

- R5.5 A failed sensor stays failed until Reset or Init, even if its reading returns to normal (no automatic recovery).

- R5.6 Temp2Enable = 0: the active sensor is always 1. Sensor 1 failed -> STOPPED.

- R5.7 Temp2Enable = 1: if the active sensor fails and the other has not, ActiveSensor switches to the other one and TempStatus reports DEGRADED (7) for as long as exactly one sensor is failed. Both failed -> STOPPED.

- R5.8 After a failover the controller does not switch back on its own; Reset returns the active sensor to 1.

- R5.9 Bad active reading, before the countdown expires: while the active sensor's raw value is NaN/Inf (or its filtered value is NaN) both relays are off immediately and the deadband countdown is cleared. The error countdown runs meanwhile (ERROR_PENDING). This is the v1 behaviour, kept.

## 6. Disagreement and relay feedback (operation continues)

- R6.1 Disagreement is evaluated only when Temp2Enable = 1, neither sensor has failed, both filtered values exist and the bit is not yet latched.

- R6.2 |Temp1Filtered - Temp2Filtered| > Temp2Tolerance for ErrorTimeout ms latches DISAGREE (bit 6). Control continues on the active sensor; the active sensor does not change.

- R6.3 With FeedbackEnable = 1 each relay's feedback input is compared with the command the controller issued on the previous call (one tick of lag is allowed by construction, more is a mismatch).

- R6.4 A mismatch held for ErrorTimeout ms latches HEATER_FB (bit 7) or COOLER_FB (bit 8). The controller keeps commanding the relays as before; it does not stop and does not change the command.

- R6.5 Once a disagreement or feedback bit is latched that check is no longer evaluated until Reset.

## 7. Heating and cooling (deadband control)

All decisions use ControlTemp = filtered value of the active sensor.

- R7.1 Idle, ControlTemp > HiBand for DeadbandTimeout ms -> cooling on. Idle, ControlTemp < LoBand for DeadbandTimeout ms -> heating on. Inside the band the countdown is cleared; crossing from one side to the other restarts it.

- R7.2 Heating stays on until ControlTemp >= Setpoint, cooling until ControlTemp <= Setpoint. Then the relay drops and the controller is idle again (so the plant is driven to the setpoint, not to the band edge).

- R7.3 Heating and cooling are mutually exclusive; while a relay is on the deadband countdown is not in play (DbRemainMs = 0).

- R7.4 DeadbandTimeout = 0 engages the relay on the first tick outside the band.

- R7.5 TempStatus when several apply, highest first:

| Code | Name | When |
| --- | --- | --- |
| 6 | STOPPED | Latched fault, relays off, until Reset. |
| 5 | ERROR_PENDING | Any error countdown is running (ErrorRemainMs > 0). |
| 8 | WARMUP | Active filter not yet full. |
| 7 | DEGRADED | Temp2Enable and exactly one sensor failed. |
| 2 | HEATING | Heating relay on. |
| 4 | COOLING | Cooling relay on. |
| 3 | COOL_PENDING | Above HiBand, deadband countdown running. |
| 1 | HEAT_PENDING | Below LoBand, deadband countdown running. |
| 0 | IN_BAND | Idle inside the band. |

Note: ERROR_PENDING, WARMUP and DEGRADED mask the control states in this code, but the relay commands in out[15..16] are always the true commands. Read the relay state from the commands, not from TempStatus.

## 8. Faults, ErrorStatus bits and return codes

- R8.1 ErrorStatus (out[17]) is a bit mask. Bits 0..8 latch until Reset or Init. Bit 9 is not latched; it follows the configuration of the current call.

| Bit | Name | Latches when | Effect on control |
| --- | --- | --- | --- |
| 0 | T1_HI | Temp1 filtered > HiLimit for ErrorTimeout | Sensor 1 failed: failover or stop. |
| 1 | T1_LO | Temp1 filtered < LoLimit for ErrorTimeout | Sensor 1 failed. |
| 2 | T1_BAD | Temp1 NaN/Inf for ErrorTimeout | Sensor 1 failed (relays already off, R5.9). |
| 3 | T2_HI | as bit 0, sensor 2 | Sensor 2 failed: failover or stop. |
| 4 | T2_LO | as bit 1, sensor 2 | Sensor 2 failed. |
| 5 | T2_BAD | as bit 2, sensor 2 | Sensor 2 failed. |
| 6 | DISAGREE | filtered sensors differ by more than Temp2Tolerance for ErrorTimeout | None, flag only. |
| 7 | HEATER_FB | heater feedback != heating command for ErrorTimeout | None, flag only. |
| 8 | COOLER_FB | cooler feedback != cooling command for ErrorTimeout | None, flag only. |
| 9 | CONFIG | configuration inconsistent (R8.3) | None, controller runs with the values as given. |

- R8.2 STOPPED (fault stop): relays off, all countdowns cleared, latched until Reset. While stopped, Step only keeps the filters running; nothing else is evaluated and ErrorRemainMs = DbRemainMs = 0. The latched bits stay visible so the cause can be read.

- R8.3 Configuration check, every call: DeadbandHi, DeadbandLo >= 0; LoLimit < LoBand and HiBand < HiLimit; both timeouts >= 0; Temp2Tolerance >= 0; FilterPoints in 0..64. A NaN in any of these fails the check. Failure sets bit 9 and returns TC_WARN_CONFIG (+1); the call still runs. FilterPoints outside 1..64 is clamped (negative or NaN -> 4, above 64 -> 64, 0 -> 4 without a warning).

- R8.4 Return value of TcStep:

| Value | Name | Meaning |
| --- | --- | --- |
| 0 | TC_OK | Ran. |
| +1 | TC_WARN_CONFIG | Ran, configuration inconsistent (bit 9 set). |
| -1 | TC_ERR_ARG | Null pointer, or in < 17 / out < 27 elements. Nothing ran. |
| -2 | TC_ERR_ZONE | zone outside 0..15. |
| -3 | TC_ERR_ACTION | action not 0, 1 or 2. |
| -4 | TC_ERR_NOT_INIT | Step on a zone that has had no Init (or Reset). |

## 9. Init and Reset

- R9.1 Init (0): clears everything in the zone, including filter history and latched bits. Active sensor = 1. Relay state is taken from in[15..16] (so a controller can be started with a relay already on, heating wins if both). The sample in the call is the first filter sample. nowMs becomes the time reference.

- R9.2 Reset (2): clears the fault stop, all latched bits (0..8) and all countdowns. Relays off, active sensor = 1. Filter history is kept, so control resumes without a new warm-up. nowMs becomes the time reference. Reset on a zone that was never initialised behaves as an Init with empty filters.

- R9.3 Neither action needs the fault to be gone: a Reset with a sensor still bad simply starts the countdown again and will stop again after ErrorTimeout.

## 10. TempSim scenarios (what the current build exercises)

| Scenario | Shows |
| --- | --- |
| warmup | Cold start: warm-up, heat pending, heating to setpoint, in-band cycling. |
| setpoint-step | Setpoint 50 -> 30 (cooler engages) -> 70. |
| sensor-failover | Sensor 1 opens: relays drop, T1_BAD after ErrorTimeout, failover to sensor 2 (degraded), sensor 1 returns but stays failed until reset. |
| both-sensors-fail | Sensor 2 sticks high (degraded), then sensor 1 opens: stopped; reset with both healthy. |
| disagree | Sensor 2 drifts +8 deg: DISAGREE bit, control continues on sensor 1. |
| feedback-fault | Heater sticks open (HEATER_FB), cooler sticks closed (COOLER_FB) and drives the plant below LoLimit until both sensors fail low and the controller stops. |
| single-sensor | One sensor, no feedback: sensor opens -> stopped; reset. |

## 11. Points I would like your view on

These are the rules most likely to need "extra rules around when faults occur". Mark any of them up or add your own.

- Sensor recovery (R5.5, R5.8). A failed sensor never recovers by itself and the controller never fails back to sensor 1. Should a sensor that reads normally for some time be re-admitted, and should control return to sensor 1 when it does?

- Feedback and disagreement bits (R6.4, R6.5). They are flags only and stay latched. Should a relay feedback mismatch stop the controller (a stuck cooler can drive the plant out of limits, see feedback-fault), and should the bits self-clear when the condition goes away?

- Disagreement with no failure (R6.2). When the two sensors disagree nothing decides which one is right; control stays on the active sensor. Should disagreement stop, or switch to the more plausible sensor?

- TempStatus priority (R7.5). ERROR_PENDING and WARMUP hide HEATING/COOLING. If the operator display should show the relay state during a countdown, the priority order or a separate field is the change.

- Bad active reading (R5.9). Relays drop at once on a NaN, before the sensor is declared failed. With Temp2Enable this means a short sensor glitch interrupts heating even though sensor 2 is healthy. Failover only happens after ErrorTimeout.

- Configuration warning (R8.3). An inconsistent configuration is reported but not refused. Should certain errors (for example HiLimit <= HiBand) force the relays off?

- Deadband return to setpoint (R7.2). A relay stays on until the setpoint is reached, not until the band edge. Confirm this is the intended overshoot behaviour for the stand.